## BuildingDesignChecklist
Building Strategy Checklist: Design Summary Tab
Project: | Enter Project Name | [6 empty] | Enter Project Name
Entry By: | Name of Person Filling In Checklist | [6 empty] | Name of Person Filling In Checklist
Phone: | Enter Phone # | [6 empty] | Enter Phone #
Email: | Enter Email | [6 empty] | Enter Email
Date: | Enter Date | [6 empty] | Enter Date
Stage: | Enter Plan Stage | [6 empty] | Enter Plan Stage
Plan: | Enter Plan Date and/or Version Name | [6 empty] | Enter Plan Date and/or Version Name
Building System Attributes--Instructions
→ Enter building design information below.
→ Drop-down lists are used in the far left column when the text begins with Pick.
→ Inputs are required in cells with bold italics red type (even if default number from formula is correct, manually type over to confirm).
→ Additional information should be entered when appropriate to the project.
→ A number of cells are locked.
→ Please enter comments liberally to note special characteristics (in the Design Comments & Simulation Comments columns to the right).
→ Reported comparisons to code only give a general indication for a particular assembly or system and are not to be used to document energy code compliance.
→ For each new design stage, you may start from the previous stage's version of this document and update as needed.
Envelope |  | MN Energy Code* 2009- | Proposed Design | % of Asssembly Area | % Better Than Code* | Design Comments | Simulation Comments | DefaultChoice | DefaultValue | DefaultPercent
Roof Insulation
| Pick 1st Roof Insulation Type | R-?? | 23.0001 | 100% | - |  |  | Pick 1st Roof Insulation Type | 23.0001 | 100%
| Pick 2nd Roof Insulation Type | R-?? | - | - | - |  |  | Pick 2nd Roof Insulation Type | 23.0001 | 0.0001%
| Pick 3rd Roof Insulation Type | R-?? | - | - | - |  |  | Pick 3rd Roof Insulation Type | 23.0001 | 0.0001%
Wall Insulation & Building Type
| Pick 1st Exterior Wall & Building Use | R-?? | 13.0001 | 100% | - |  |  | Pick 1st Exterior Wall & Building Use | 13.0001 | 100%
| Pick 2nd Exterior Wall & Building Use | R-?? | - | - | - |  |  | Pick 2nd Exterior Wall & Building Use | 13.0001 | 0.0001%
| Pick 3rd Exterior Wall & Building Use | R-?? | - | - | - |  |  | Pick 3rd Exterior Wall & Building Use | 13.0001 | 0.0001%
Infiltration Reduction
| Pick 1st Special Feature to Minimize Infiltration |  |  | 100% | - |  |  | Pick 1st Special Feature to Minimize Infiltration |  | 100%
| Pick 2nd Special Feature to Minimize Infiltration |  |  | - | - |  |  | Pick 2nd Special Feature to Minimize Infiltration |  | 0.0001%
| Pick 3rd Special Feature to Minimize Infiltration |  |  | - | - |  |  | Pick 3rd Special Feature to Minimize Infiltration |  | 0.0001%
Window Area & Performance
| % Window to Gross Wall Area | 50% | 25% |  | 50% |  |  |  | 0.25
|  | North Wall % Window to Wall Area | 25% | - | - |  |  |  | 25% | 25%
|  | South Wall % Window to Wall Area | 25% | - | - |  |  |  | 25% | 25%
|  | East & West Walls % Window to Wall Area | 25% | - | - |  |  |  | 25% | 25%
| 1st Fixed Vertical Glazing Type | U-0.57 | 0.35 | 100% | 38.6% |  |  | 1st Fixed Vertical Glazing Type | 0.35 | 100%
| Pick Climate Zone | <---- <---- <---- | 0.39 |  | - |  |  | Pick Climate Zone | 0.39
| 1st Operable Vertical Glazing Type | U-0.67 | 0.35 | 0.0001% | 47.76% |  |  | 1st Operable Vertical Glazing Type | 0.35 | 0.0001%
| Pick Climate Zone | <---- <---- <---- | 0.39 |  | - |  |  | Pick Climate Zone | 0.39
| 2nd Fixed Vertical Glazing Type | U-0.57 | - | - | - |  |  | 2nd Fixed Vertical Glazing Type | 0.35 | 0.0001%
|  | SHGC-0.49 (0.64 North) | - |  | - |  |  |  | 0.39
| 2nd Operable Vertical Glazing Type | U-0.67 | - | - | - |  |  | 2nd Operable Vertical Glazing Type | 0.35 | 0.0001%
|  | SHGC-0.49 (0.64 North) | - |  | - |  |  |  | 0.39
| Glazing At Semiheated Area--Fixed | U-1.22 | - | - | - |  |  | Glazing At Semiheated Area--Fixed | 0.35 | 0.0001%
| Glazing At Semiheated Area--Operable | U-1.27 | - | - | - |  |  | Glazing At Semiheated Area--Operable | 0.39 | 0.0001%
Orientation & Other Envelope Features
| Building Orientation: % of Exterior Exposure Facing North or South |  |  | 50% | [5 empty] | 50%
| 1st Additional Building Envelope Special Energy Feature |  | - | - | -
| 2nd Additional Building Envelope Special Energy Feature |  | - | - | -
| 3rd Additional Building Envelope Special Energy Feature |  | - | - | -
†Continuous insulation (as opposed to insulation in a cavity with studs or other thermal bridging structure) is denoted by "ci".
Lighting Power Density & Control |  | MN Energy Code* 2009- | Proposed Design | % of Project Area | % Better Than Code* | Design Comment | Simulation Comments
| Pick 1st Building Type | <---- <---- <---- | 1.0001 | 100% | - |  |  | Pick 1st Building Type | 1.0001 | 100%
| Pick 2nd Building Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Building Type | 1.0001 | 0.0001%
| Pick 3rd Building Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Building Type | 1.0001 | 0.0001%
| Daylighting With Automatic Photocell Control |  | - | 0.0001% | - |  |  |  |  | 0.0001%
| Daylighting With Manual Control (e.g. Perimter Offices with Switches) |  |  | 0.0001% | - |  |  |  |  | 0.0001%
| Occupancy Sensor Control of Rooms |  | - | 0.0001% | - |  |  |  |  | 0.0001%
| Scheduled Control of Lighting (e.g. BAS After Hours Sweep) |  | - | 0.0001% | - |  |  |  |  | 0.0001%
†Lighting power density in units of Watts per square foot are denoted by wsf.
HVAC |  | MN Energy Code* 2009- | Proposed Design | % of Area Served | % Better Than Code*,† | Design Comments | Simulation Comments | DefaultChoice | DefaultValue | DefaultPercent
Air Handler Types, Ventilation Control & Fan Power
| Pick 1st Air Handler Type | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Air Handler Type |  | 100%
| Pick 2nd Air Handler Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Air Handler Type |  | 0.0001%
| Pick 3rd Air Handler Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Air Handler Type |  | 0.0001%
| Pick 4th Air Handler Type | <---- <---- <---- | - | - | - |  |  | Pick 4th Air Handler Type |  | 0.0001%
| Air Side Economizer (Required 3,000+cfm air flow systems) | 0.0001% | - | 0.0001% | - |  |  | Air Side Economizer |  | 0.0001%
| Area With Demand Control Ventilation (Required for 500+sf high occupancy spaces) | 0.0001% | - | 0.0001% | - |  |  | Pick 1st Ventilation Control |  | 0.0001%
| Area With Energy Recovery Ventilation (Required where 5,000+cfm & 70%+ outside air) | 0.0001% | - | 0.0001% | - |  |  | Pick 1st Energy Recovery Ventilation Type |  | 0.0001%
| Max Duct Static Pressure |  | - | - | - |  |  | Max Duct Static Pressure |  | 0.0001%
| Note Any Low Fan Power Feature(s) |  | - | - | - |  |  | Note Any Low Fan Power Feature(s) |  | 0.0001%
Central Heat
| Pick 1st Central Heat Source Type | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Central Heat Source Type | 80% | 100%
| Pick 2nd Central Heat Source Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Central Heat Source Type | 80% | 0.0001%
| Pick 3rd Central Heat Source Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Central Heat Source Type | 80% | 0.0001%
Heat at Air Handlers
| Pick 1st Heat Source at Air Handler(s) | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Heat Source at Air Handler(s) | 80% | 100%
| Pick 2nd Heat Source at Air Handler(s) | <---- <---- <---- | - | - | - |  |  | Pick 2nd Heat Source at Air Handler(s) | 80% | 0.0001%
| Pick 3rd Heat Source at Air Handler(s) | <---- <---- <---- | - | - | - |  |  | Pick 3rd Heat Source at Air Handler(s) | 80% | 0.0001%
Heat at Zones
| Pick 1st Heat Source at Zone(s) | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Heat Source at Zone(s) | 80% | 100%
| Pick 2nd Heat Source at Zone(s) | <---- <---- <---- | - | - | - |  |  | Pick 2nd Heat Source at Zone(s) | 80% | 0.0001%
| Pick 3rd Heat Source at Zone(s) | <---- <---- <---- | - | - | - |  |  | Pick 3rd Heat Source at Zone(s) | 80% | 0.0001%
Central Cooling
| Pick 1st Central Cooling Source Type | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Central Cooling Source Type | 80% | 100%
| Pick 2nd Central Cooling Source Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Central Cooling Source Type |  | 0.0001%
| Pick 3rd Central Cooling Source Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Central Cooling Source Type |  | 0.0001%
Cooling at Air Handlers
| Pick 1st Cooling Source at Air Handler(s) | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Cooling Source at Air Handler(s) | 12.0001 | 100%
| Pick 2nd Cooling Source at Air Handler(s) | <---- <---- <---- | - | - | - |  |  | Pick 2nd Cooling Source at Air Handler(s) | 12.0001 | 0.0001%
| Pick 3rd Cooling Source at Air Handler(s) | <---- <---- <---- | - | - | - |  |  | Pick 3rd Cooling Source at Air Handler(s) | 12.0001 | 0.0001%
Cooling at Zones
| Pick 1st Cooling Source at Zone(s) | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Cooling Source at Zone(s) | 12.0001 | 100%
| Pick 2nd Cooling Source at Zone(s) | <---- <---- <---- | - | - | - |  |  | Pick 2nd Cooling Source at Zone(s) | 12.0001 | 0.0001%
| Pick 3rd Cooling Source at Zone(s) | <---- <---- <---- | - | - | - |  |  | Pick 3rd Cooling Source at Zone(s) | 12.0001 | 0.0001%
Additional HVAC Efficiency Features
| 1st Special Feature (Add Comment) | - | - | - | - |  |  | 1st Special Feature (Add Comment) |  | 0.0001%
| 2nd Special Feature (Add Comment) | - | - | - | - |  |  | 2nd Special Feature (Add Comment) |  | 0.0001%
| 3rd Special Feature (Add Comment) | - | - | - | - |  |  | 3rd Special Feature (Add Comment) |  | 0.0001%
| 4th Special Feature (Add Comment) | - | - | - | - |  |  | 4th Special Feature (Add Comment) |  | 0.0001%
†Displayed '% Better Than Code" values do not consider the energy impact of HVAC system type changes, but rather only the proposed efficiency compared to the minimum energy code requirement for the given type of equipment in the proposed design.
Equipment/Process Load Energy Efficiency |  | Baseline Design | Proposed Design | % of Project Area | % Better Than Baseline | Design Comments | Simulation Comments
| EnergyStar Computers |  | - | 0.0001% | - |  |  |  |  | 0.0001%
| EnergyStar Office Equipment (Copiers, Fax Machines, Etc.) |  | - | 0.0001% | - |  |  |  |  | 0.0001%
Other Equipment or Process Energy Savings Features
| 1st Special Feature (Add Comment) | - | - | - | - |  |  | 1st Special Feature (Add Comment) |  | 0.0001%
| 2nd Special Feature (Add Comment) | - | - | - | - |  |  | 2nd Special Feature (Add Comment) |  | 0.0001%
| 3rd Special Feature (Add Comment) | - | - | - | - |  |  | 3rd Special Feature (Add Comment) |  | 0.0001%
| 4th Special Feature (Add Comment) | - | - | - | - |  |  | 4th Special Feature (Add Comment) |  | 0.0001%
-
-
Domestic Water Heating |  | MN Energy Code* 2009- | Proposed Design | % of Load | % Better Than Code* | Design Comments | Simulation Comments
| Pick 1st Water Heater Type | <---- <---- <---- | - | 100% | - |  |  | Pick 1st Water Heater Type | 0.6201 | 100% | 0.9001 | 80.01% | 260.0001 | 80% Et, 900 SL
| Pick 2nd Water Heater Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Water Heater Type | 0.6201 | 0.0001% | 0.9001 | 80.01% | 260.0001 | 80% Et, 900 SL
| Pick 3rd Water Heater Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Water Heater Type | 0.6201 | 0.0001% | 0.9001 | 80.01% | 260.0001 | 80% Et, 900 SL
Hot Water Load Reduction Features
| 1st Special Feature (Add Comment) | - | - | - | - |  |  | 1st Special Feature (Add Comment) |  | 0.0001%
| 2nd Special Feature (Add Comment) | - | - | - | - |  |  | 2nd Special Feature (Add Comment) |  | 0.0001%
| 3rd Special Feature (Add Comment) | - | - | - | - |  |  | 3rd Special Feature (Add Comment) |  | 0.0001%
| 4th Special Feature (Add Comment) | - | - | - | - |  |  | 4th Special Feature (Add Comment) |  | 0.0001%
Use of Renewables |  |  |  | % of Load |  | Design Comments | Simulation Comments | Fuel Types
| Pick 1st Renewable Type | <---- <---- <---- | - | - | - |  |  | Pick 1st Renewable Type |  | 2%
| Pick 2nd Renewable Type | <---- <---- <---- | - | - | - |  |  | Pick 2nd Renewable Type |  | 2%
| Pick 3rd Renewable Type | <---- <---- <---- | - | - | - |  |  | Pick 3rd Renewable Type |  | 2%
| Pick 4th Renewable Type | <---- <---- <---- | - | - | - |  |  | Pick 4th Renewable Type |  | 2%
2%
Other Energy Features or Comments |  |  |  | % of Load |  | Design Comments | Simulation Comments | Fuel Types
| 1st Special Feature (Add Comment) | - | - | - | - |  |  | Pick 1st Renewable Type |  | 2%
| 2nd Special Feature (Add Comment) | - | - | - | - |  |  | Pick 2nd Renewable Type |  | 2%
| 3rd Special Feature (Add Comment) | - | - | - | - |  |  | Pick 3rd Renewable Type |  | 2%
| 4th Special Feature (Add Comment) | - | - | - | - |  |  | Pick 4th Renewable Type |  | 2%
2%
*The general listing of Minnestoa Energy Code efficiency levels is only meant for rough comparisons for a limited number of common items, and is neither an official nor comprehensive indication of Minnesota Energy Code requirements for specific projects.

## LPD Lookup (hidden)
From ASHRAE 90.1 2004
Building Level Lighting Power Density
Building Type |  | wsf
Pick 1st Building Type | <---- <---- <---- | <---- <---- <----
Pick 2nd Building Type | <---- <---- <---- | <---- <---- <----
Pick 3rd Building Type | <---- <---- <---- | <---- <---- <----
Automotive Facility | 0.9 | 0.9
Convention Center | 1.2 | 1.2
Court House | 1.2 | 1.2
Dining: Bar Lounge/Leisure | 1.3 | 1.3
Dining: Cafeteria/Fast Food | 1.4 | 1.4
Dining: Family | 1.6 | 1.6
Dormitory | 1 | 1.0
Exercise Center | 1 | 1.0
Gymnasium | 1.1 | 1.1
Health Care-Clinic | 1 | 1.0
Hospital | 1.2 | 1.2
Hotel | 1 | 1.0
Library | 1.3 | 1.3
Manufacturing Facility | 1.3 | 1.3
Motel | 1 | 1.0
Motion Picture Theater | 1.2 | 1.2
Multi-Family | 0.7 | 0.7
Museum | 1.1 | 1.1
Office | 1 | 1.0
Parking Garage | 0.3 | 0.3
Penitentiary | 1 | 1.0
Performing Arts Theater | 1.6 | 1.6
Police/Fire Station | 1 | 1.0
Post Office | 1.1 | 1.1
Religious Building | 1.3 | 1.3
Retail | 1.5 | 1.5
School/University | 1.2 | 1.2
Sports Arena | 1.1 | 1.1
Town Hall | 1.1 | 1.1
Transportation | 1 | 1.0
Warehouse | 0.8 | 0.8
Workshop | 1.4 | 1.4

## Lists_LookupTables (hidden)
ERV Table | Do we need ERV effectiveness entered??? |  | DCV Table |  |  | EconomizerTable |  | Must be in alphabetical order | Check with Mark H & Martha | CoolTable |  |  | HeatTable |  |  | Residential water heater EF is based on size--40 gallon assumed
ERV Options | HtCoolSvgs | FanSvgs | DCV Options | HtCoolSvgs | FanSvgs | EconomizerOptions | CoolSvgs | LightingControls | Light Svgs | ACrating | Standard | MNCode2009 | HeatRatings | Standard | MNCode2009 | SHWratings | Standard | SHWload | ProcessLoadUnits | Outdoor Air Flow Based On
Heating and Cooling | 70% | -10% | Carbon Dioxide Sensor(s) | 30% | 10% | No Economizer | 0% | Auto Off Plus Daylighting | 25% | EER (6-11.5 tons) | 8.3 | 10.1 | Boiler (Commercial)--Et | 75% | 75% | Energy Factor (Residential) | 52.4% | Gallons/Day | BTU/Hour | Default Estimate (20% OA)
Heating Only | 60% | -10% | None | 0% | 0% | Select Economizer | 0% | Auto Off (Occupancy Sensor) | 10% | IPLV (6-11.5 tons) | 7.3 | 11.2 | Boiler (Residential)--AFUE | 68% | 80% | Et (>100 gal or 75,000 Btu/hr) | 76% | Gallons/Hour | BTU/Year | Final Design
None | 0% | 0% | Motion Sensor(s) | 20% | 10% | Yes--Dry Bulb | 20% | Automatic Daylighting | 20% | SEER (< 6 tons) | 8.6 | 12 | Furnace (Commercial)--Et | 75% | 80% | Select Rating | Based On---> | Gallons/Minute | kW (kiloWatts) | Manual Estimate
Select ERV | 0% | 0% | Select DCV Control | 0% | 0% | Yes--Enthaly | 25% | Continuous or Manual | 0% | Select Rating | Based On---> | --> --> --> --> | Furnace (Residential)--AFUE | 68% | 78% |  |  | Gallons/Year | kWh/Day (kiloWatt Hours)
[8 empty] | Select Control | 0% |  |  |  | Select Rating | Based On--> | --> --> --> --> |  |  | Select Units | kWh/Year (kiloWatt Hours)
Must be in alphabetical order |  |  | Must be in alphabetical order | [9 empty] | Unit Heater/Duct Furnace--Ec | 75% | 80% |  |  |  | Select Units
Must be in alphabetical order

## NewLookUps (hidden)
RoofRTbl
RoofRTblList
Pick 1st Roof Insulation Type | R-??
Pick 2nd Roof Insulation Type | R-??
Pick 3rd Roof Insulation Type | R-??
All Insulation Above Deck | R-23 ci†
Insulation NOT All Above Deck | R-30
Semiheated--All Insulation Above Deck | R-16.6 ci†
Semiheated--Insulation NOT All Above Deck | R-19
WallRTbl
WallRTblList
Pick 1st Exterior Wall & Building Use | R-??
Pick 2nd Exterior Wall & Building Use | R-??
Pick 3rd Exterior Wall & Building Use | R-??
Mass Wall Exterior (Nonresidential) | R-9.5 ci†
Mass Wall Exterior (Residential) | R-11.4 ci†
Mass Wall Exterior (Semiheated) | None
Metal Wall Exterior (Nonresidential) | R-13
Metal Wall Exterior (Residential) | R-13 + R-13 ci†
Metal Wall Exterior (Semiheated) | R-13
Steel Framed Exterior Wall (Nonresidential) | R-13 + R-3.8 ci†
Steel Framed Exterior Wall (Residential) | R-13 + R-7.5 ci†
Steel Framed Exterior Wall (Semiheated) | R-13
Wood Framed Ext. Wall (Residential)-Northern MN | R-13 + R-7.5 ci†
Wood Framed Ext. Wall (Residential)-Southern MN | R-13 + R-3.8 ci†
Wood Framed Exterior Wall (Nonresidential) | R-13
Wood Framed Exterior Wall (Semiheated) | R-13
ClimateZone
Pick Climate Zone
Northern Minnesota (Zone 7)
Southern Minnesota (Zone 6A)
InfiltrationTbl
Pick 1st Special Feature to Minimize Infiltration
Pick 2nd Special Feature to Minimize Infiltration
Pick 3rd Special Feature to Minimize Infiltration
Air Leakage Testing (Note Target in Comment)
Commisisoning of Envelope
Detail Air Barrier at All Transitions (e.g. Roof-Wall)
Exterior Finish Insulation System (Prefab)
Exterior Hight Density Spray Foam
Interior High Density Spray Foam
None (Air Barrier Noted on Plans)
Other (Add Comment to the Far Right)
Structurally Insulated Panels
CentralHtTbl
CentralHtList | MNCode2009
Pick 1st Central Heat Source Type | <---- <---- <----
Pick 2nd Central Heat Source Type | <---- <---- <----
Pick 3rd Central Heat Source Type | <---- <---- <----
Combined Heat & Power Boiler | -
District Hot Water | -
District Steam | -
Electric Boiler | -
Gas Boiler (Commercial)--Hot Water [Et] | 75%
Gas Boiler (Commercial)--Steam [Et] | 75%
Gas Boiler (Residential)--AFUE | 80%
Ground Coupled Heat Pump Loops--Horizontal | -
Ground Coupled Heat Pump Loops--Vertical | -
Groundwater or Pond Heat Pump Loop | -
Heat Recovery from… (Add Comment to the Right) | -
No Central Heating Plant | -
Other (Add Comment to the Far Right) | -
Solar Thermal Panel | -
Solar Thermal Tube | -
Variable Refrigerant Flow Condensing Unit | -
AirHandlerTypeTbl
AirHandlerTypeList
Pick 1st Air Handler Type | <---- <---- <----
Pick 2nd Air Handler Type | <---- <---- <----
Pick 3rd Air Handler Type | <---- <---- <----
Pick 4th Air Handler Type | <---- <---- <----
Constant Volume Multi-Zone Unit(s) | -
Constant Volume Single Zone Unit(s) | -
Dedicated Outdoor Air System (in Tandem with Other System[s])
Make-Up Air Unit (No Other Handler for the Area) | -
None | -
Other (Add Comment to the Right) | -
VAV Multiple Zones | -
VAV Single Zone(s) | -
ERVTbl
ERVList
No Energy Recovery Ventilation | Req'd if 5,000+ cfm & 70+% OA
Pick 1st Energy Recovery Ventilation Type | <---- <---- <----
Pick 2nd Energy Recovery Ventilation Type | <---- <---- <----
Air to Air ERV Heat Exchanger--Heat Only | Req'd if 5,000+ cfm & 70+% OA | ~60% of outside air load
Air to Air ERV Heat Exchanger--Heat & Cool | Req'd if 5,000+ cfm & 70+% OA | ~70% of outside air load
Enthalpy Wheel ERV | Req'd if 5,000+ cfm & 70+% OA | ~70% of outside air load
Heat Pipe ERV Heat Exchanger--Heat Only | Req'd if 5,000+ cfm & 70+% OA | ~60% of outside air load
Heat Pipe ERV Heat Exchanger--Heat & Cool | Req'd if 5,000+ cfm & 70+% OA | ~70% of outside air load
Thermal Wheel ERV--Heat Only | Req'd if 5,000+ cfm & 70+% OA | ~60% of outside air load
Thermal Wheel ERV--Heat & Cool | Req'd if 5,000+ cfm & 70+% OA | ~60% of outside air load
Water Coil Type ERVs--Heat Only | Req'd if 5,000+ cfm & 70+% OA | ~50% of outside air load
Water Coil Type ERVs--Heat & Cool | Req'd if 5,000+ cfm & 70+% OA | ~55% of outside air load
VentilationControlTbl
VentilationControlList
No Demand Ventilation Control | Req'd in high occupancy >500sf
Pick 1st Demand Ventilation Control | <---- <---- <----
Pick 2nd Demand Ventilation Control | <---- <---- <----
Pick 3rd Demand Ventilation Control | <---- <---- <----
Carbon Dioxide Sensor(s) in Return Duct | Req'd in high occupancy >500sf
Carbon Dioxide Sensor(s) in Space | Req'd in high occupancy >500sf
Carbon Monoxide Sensor(s) in Space | Not Required
Occupancy Sensor(s) | Req'd in high occupancy >500sf
Other (Add Comment to the Right) | Req'd in high occupancy >500sf
AirHandlerHtTbl
AirHandlerHtList
Pick 1st Heat Source at Air Handler(s) | <---- <---- <----
Pick 2nd Heat Source at Air Handler(s) | <---- <---- <----
Pick 3rd Heat Source at Air Handler(s) | <---- <---- <----
Duct Furnace--Electric Resistance | -
Duct Furnace--Gas (Ec) | 80%
Electric Resistance Coil in Duct | -
Gas Furnace (Commercial ≥ 225,000 Btu/hr)--Et | 80%
Gas Furnace (Residential < 225,000 Btu/hr)--AFUE | 78%
Heat Pump--Air Source: 5 tons or less (per unit) | 7.4 hspf
Heat Pump--Air Source: from 5 to 11 tons (per unit) | 3.2 COP
Heat Pump--Air Source: more than 11 tons (per unit) | 3.1 COP
Heat Pump--Ground Source | 3.1 COP
Heat Pump--Groundwater Source | 3.6 COP
Heat Pump--Water Loop | 4.2 COP
Heat Recovery from AC Condenser | -
Heat Recovery from… (Add Comment to the Right) | -
Glycol Coil(s) | -
Hot Water Coil(s) | -
None | -
None--All Heat at Zone Level | -
Other (Add Comment to the Right) | -
Run-Around Reheat Coil | -
Steam Coil(s) | -
Unit Heater--Electric | -
Unit Heater--Gas (Ec) | 80%
Variable Refrigerant Flow--(Pick Heat Pump & Comment) | <---- <---- <----
ZoneHtTbl
ZoneHtList
Pick 1st Heat Source at Zone(s) | <---- <---- <----
Pick 2nd Heat Source at Zone(s) | <---- <---- <----
Pick 3rd Heat Source at Zone(s) | <---- <---- <----
Baseboard Radiation--Electric | -
Baseboard Radiation--Hot Water | -
Electric Resistance Heating Coil | -
Electric Resistance Reheat | -
Gas Furnace (Commercial ≥ 225,000 Btu/hr)--Et | 80%
Gas Furnace (Residential < 225,000 Btu/hr)--AFUE | 78%
Heat Pump--Air Source: 5 tons or less (per unit) | 7.4 hspf
Heat Pump--Air Source: from 5 to 11 tons (per unit) | 3.2 COP
Heat Pump--Air Source: more than 11 tons (per unit) | 3.1 COP
Heat Pump--Ground Source | 3.1 COP
Heat Pump--Groundwater Source | 3.6 COP
Heat Pump--Water Loop | 4.2 COP
Heat Recovery from AC Condenser | -
Heat Recovery from… (Add Comment to the Right) | -
Hot Water Heating Coil(s) | -
Hot Water Reheat Coil(s) | -
None | -
None--All Heat at Air Handler Level | -
Other (Add Comment to the Right) | -
Packaged Terminal Heat Pump: 0.5 ton | 3.0 COP
Packaged Terminal Heat Pump: 1.0 ton | 2.9 COP
Packaged Terminal Heat Pump: 1.5 ton | 2.7 COP
Radiant Floor--Electric | -
Radiant Floor--Hot Water | -
Radiant Tube--Gas Fired | -
Radiant Panel--Electric | -
Radiant Panel--Hot Water | -
Radiant--High Intensity Electric | -
Radiant--High Intensity Gas | -
Radiator(s)--Panel or Cabinet--Electric | -
Radiator(s)--Panel or Cabinet--Hot Water | -
Radiator(s)--Panel or Cabinet--Steam | -
Run-Around Reheat Coil | -
Steam Coil(s) | -
Unit Heater--Electric | -
Unit Heater--Gas (Ec) | 80%
Variable Refrigerant Flow--(Pick Heat Pump & Comment) | <---- <---- <----
CentralCoolTbl
CentralCoolList
Pick 1st Central Cooling Source Type | <---- <---- <----
Pick 2nd Central Cooling Source Type | <---- <---- <----
Pick 3rd Central Cooling Source Type | <---- <---- <----
Absorption Chiller--Double Effect, Direct-Fired | 1.00 COP, 1.00 IPLV
Absorption Chiller--Double Effect, Indirect-Fired | 1.00 COP, 1.05 IPLV
Absorption Chiller--Single Effect, Air Cooled | 0.60 COP
Absorption Chiller--Single Effect, Water Cooled | 0.70 COP
Air-Cooled Condenser | ³176,000 Btu/hr/hp
Centrifugal Chiller & Air Cooled Condenser | 2.80 COP, 3.05 IPLV
Centrifugal Chiller--Water Cooled: <150 tons | 5.00 COP, 5.25 IPLV
Centrifugal Chiller--Water Cooled: From 150 up to 299.9 tons | 5.55 COP, 5.90 IPLV
Centrifugal Chiller--Water Cooled: More Than 299.9 tons | 6.10 COP, 6.40 IPLV
Cooling Tower--Axial/Propeller Fan | ³38.2 gpm/hp
Cooling Tower--Centrifugal Fan | ³20.0 gpm/hp
District Energy Chilled Water | -
Other (Add Comment to the Right) | -
Reciprocating Chiller & Air Cooled Condenser | 2.80 COP, 3.05 IPLV
Reciprocating Chiller--Water Cooled: All Sizes | 4.20 COP, 5.05 IPLV
Screw Chiller & Air Cooled Condenser | 2.80 COP, 3.05 IPLV
Screw Chiller--Water Cooled: <150 tons | 4.45 COP, 5.20 IPLV
Screw Chiller--Water Cooled: From 150 up to 299.9 tons | 4.90 COP, 5.60 IPLV
Screw Chiller--Water Cooled: More Than 299.9 tons | 5.50 COP, 6.15 IPLV
Scroll Chiller & Air Cooled Condenser | 2.80 COP, 3.05 IPLV
Scroll Chiller--Water Cooled: <150 tons | 4.45 COP, 5.20 IPLV
Scroll Chiller--Water Cooled: From 150 up to 299.9 tons | 4.90 COP, 5.60 IPLV
Scroll Chiller--Water Cooled: More Than 299.9 tons | 5.50 COP, 6.15 IPLV
Variable Refrigerant Flow Condensing Unit | -
Water Side Economizer | -
AirHandlerCoolTbl
AirHandlerCoolList
Pick 1st Cooling Source at Air Handler(s) | <---- <---- <----
Pick 2nd Cooling Source at Air Handler(s) | <---- <---- <----
Pick 3rd Cooling Source at Air Handler(s) | <---- <---- <----
Chilled Water Coil(s) | -
Desiccant Unit--Direct Fired | -
Desiccant Unit--Indirect Fired (Internal Boiler) | -
DX: ≤5 tons (per unit) | 12.0 SEER
DX: > 5 tons up to 11 tons (per unit), Electric or No Heat | 10.3 EER
DX: > 5 tons up to 11 tons (per unit), Gas or HW Heat | 10.1 EER
DX: >11 tons and <20 tons (per unit), Gas or HW Heat | 9.5 EER
DX: >11 tons and <20 tons (per unit), Electric or No Heat | 9.7 EER
DX: ≥ 20 tons and <63.3 tons (per unit), Electric or No Heat | 9.5 EER, 9.7 IPLV
DX: ≥ 20 tons and <63.3 tons (per unit), Gas or HW Heat | 9.3 EER, 9.5 IPLV
DX: ≥ 63.3 tons (per unit), Electric or No Heat | 9.2 EER, 9.4 IPLV
DX: ≥ 63.3 tons (per unit), Heat | 9.0 EER, 9.2 IPLV
Energy Recovery Ventilation--Sensible Only | -
Energy Recovery Ventilation--Total Enthalpy | -
Evaporative Cooling--Directly in Supply Air | -
Evaporative Cooling--Direct/Indirect | -
Heat Pump--Air Source: ≤5 tons (per unit) | 12.0 SEER
Heat Pump--Air Source: > 5 tons up to 11 tons, Electric Backup | 10.1 EER
Heat Pump--Air Source: > 5 tons up to 11 tons, Gas or HW Backup | 9.9 EER
Heat Pump--Air Source: >11 tons and <20 tons, Electric Backup | 9.3 EER
Heat Pump--Air Source: >11 tons and <20 tons, Gas or HW Backup | 9.1 EER
Heat Pump--Air Source: ≥ 20 tons (per unit), Electric Backup | 9.0 EER, 9.2 IPLV
Heat Pump--Air Source: ≥ 20 tons(per unit), Gas or HW Backup | 8.8 EER, 9.0 IPLV
Heat Pump--Ground Source | 13.4 EER
Heat Pump--Groundwater Source | 16.2 EER
Heat Pump--Water Loop: < 1.5 tons | 11.2 EER
Heat Pump--Water Loop: 1.5 up to 11 tons | 12.0 EER
Heat Pump--Water Loop: 11+ tons | -
None | -
None--All Cooling at Zone Level | -
Other (Add Comment to the Right) | -
Run-Around Coil | -
Variable Refrigerant Flow--(Pick DX or Heat Pump & Comment) | <---- <---- <----
ZoneCoolTbl
ZoneCoolList
Pick 1st Cooling Source at Zone(s) | <---- <---- <----
Pick 2nd Cooling Source at Zone(s) | <---- <---- <----
Pick 3rd Cooling Source at Zone(s) | <---- <---- <----
Chilled Beams | -
Chilled Water Coil(s) | -
DX: ≤5 tons (per unit) | 12.0 SEER
DX: > 5 tons up to 11 tons (per unit), Electric or No Heat | 10.3 EER
DX: > 5 tons up to 11 tons (per unit), Gas or HW Heat | 10.1 EER
DX: >11 tons and <20 tons (per unit), Gas or HW Heat | 9.5 EER
DX: >11 tons and <20 tons (per unit), Electric or No Heat | 9.7 EER
DX: ≥ 20 tons and <63.3 tons (per unit), Electric or No Heat | 9.5 EER, 9.7 IPLV
DX: ≥ 20 tons and <63.3 tons (per unit), Gas or HW Heat | 9.3 EER, 9.5 IPLV
DX: ≥ 63.3 tons (per unit), Electric or No Heat | 9.2 EER, 9.4 IPLV
DX: ≥ 63.3 tons (per unit), Heat | 9.0 EER, 9.2 IPLV
Energy Recovery Ventilation--Sensible Only | -
Energy Recovery Ventilation--Total Enthalpy | -
Evaporative Cooling--Directly in Supply Air | -
Evaporative Cooling--Direct/Indirect | -
Heat Pump--Air Source: ≤5 tons (per unit) | 12.0 SEER
Heat Pump--Air Source: > 5 tons up to 11 tons, Electric Backup | 10.1 EER
Heat Pump--Air Source: > 5 tons up to 11 tons, Gas or HW Backup | 9.9 EER
Heat Pump--Air Source: >11 tons and <20 tons, Electric Backup | 9.3 EER
Heat Pump--Air Source: >11 tons and <20 tons, Gas or HW Backup | 9.1 EER
Heat Pump--Air Source: ≥ 20 tons (per unit), Electric Backup | 9.0 EER, 9.2 IPLV
Heat Pump--Air Source: ≥ 20 tons(per unit), Gas or HW Backup | 8.8 EER, 9.0 IPLV
Heat Pump--Ground Source | 13.4 EER
Heat Pump--Groundwater Source | 16.2 EER
Heat Pump--Water Loop: < 1.5 tons | 11.2 EER
Heat Pump--Water Loop: 1.5 up to 11 tons | 12.0 EER
Heat Pump--Water Loop: 11+ tons | -
None | -
None--All Cooling at Air Handler Level | -
Other (Add Comment to the Right) | -
Packaged Terminal Air Conditioner: 0.5 ton | 11.2 EER
Packaged Terminal Air Conditioner: 1.0 ton | 9.9 EER
Packaged Terminal Air Conditioner: 1.5 ton | 8.7 EER
Packaged Terminal Heat Pump: 0.5 ton | 11.0 EER
Packaged Terminal Heat Pump: 1.0 ton | 9.7 EER
Packaged Terminal Heat Pump: 1.5 ton | 8.5 EER
Passive Ventilation | -
Radiant Floor | -
Radiant Panel | -
Room AC, with Louvered Sides: <20,000 Btu/hr | 9.7 EER
Room AC, with Louvered Sides: ≥20,000 Btu/hr | 8.5 EER
Room AC, without Louvered Sides: <8,000 Btu/hr | 9.0 EER
Room AC, without Louvered Sides: ≥8,000 Btu/hr | 8.5 EER
Run-Around Coil | -
Variable Refrigerant Flow--(Pick DX or Heat Pump & Comment) | <---- <---- <----
HWHtrTbl
HWHtrList
Pick 1st Water Heater Type | <---- <---- <----
Pick 2nd Water Heater Type | <---- <---- <----
Pick 3rd Water Heater Type | <---- <---- <----
Condenser Heat Recovery | -
Electric Resistance--Instantaneous | -
Electric Resistance--Tank Type, (> 12 kW), 50 gal | SL ≤ 267 Btu/hr |  | 267.4874 | 50
Electric Resistance--Tank Type, (> 12 kW), 80 gal | SL ≤ 333 Btu/hr |  | 333.0495 | 80
Electric Resistance--Tank Type, (≤ 12 kW), 20 gal | 0.90 EF |  | 0.9036 | 20
Electric Resistance--Tank Type, (≤ 12 kW), 40 gal | 0.88 EF |  | 0.8772 | 40
Electric Resistance--Tank Type, (≤ 12 kW), 60 gal | 0.85 EF |  | 0.8508 | 60
Gas--Instantaneous, (<200,000 Btu/hr) | 0.62 EF |  |  | gal | Btu/hr
Gas--Instantaneous, (≥200,000 Btu/hr) | 80% Et
Gas--Tank Type, (>75,000 Btu/hr), 50 gal | 80% Et, SL ≤ ~900 Btu/hr |  | 902.8175 | 50 | 100000
Gas--Tank Type, (>75,000 Btu/hr), 80 gal | 80% Et, SL ≤ ~1,230 Btu/hr |  | 1233.8699 | 80 | 200000
Gas--Tank Type, (≤75,000 Btu/hr), 20 gal | 0.58 EF |  | 0.582 | 20
Gas--Tank Type, (≤75,000 Btu/hr), 40 gal | 0.54 EF |  | 0.544 | 40
Heat Exchanger With Boiler--Seasonal | -
Heat Exchanger With Boiler--Year Round | -
Heat Pump--Tank Type, (≤ 24A & ≤250V), 20 gal | 0.90 EF |  | 0.9036 | 20
Heat Pump--Tank Type, (≤ 24A & ≤250V), 40 gal | 0.88 EF |  | 0.8772 | 40
Heat Pump--Tank Type, (≤ 24A & ≤250V), 60 gal | 0.85 EF |  | 0.8508 | 60
Heat Recovery--AC Condenser | -
Heat Recovery--AC Desuperheater
Heat Recovery--Other (Add Comment) | -
Heat Recovery--Refrigeration Condenser | -
Heat Recovery--Refrigeration Desuperheater | -
Solar Thermal--Flat Plate | -
Solar Thermal--Tube | -
RenewablesTbl
RenewablesList
Pick 1st Renewable Type | <---- <---- <----
Pick 2nd Renewable Type | <---- <---- <----
Pick 3rd Renewable Type | <---- <---- <----
Pick 4th Renewable Type | <---- <---- <----
On-Site Wind | -
Other Renewable (Add Comment) | -
Passive Solar Heating | -
Solar PV | -
Solar Thermal--Domestic Hot Water | -
Solar Thermal--Outdoor Air Preheating | -
Solar Thermal--Space Heating | -