## App I-4
APPENDIX I-4 Calculating CO2 Concentrations in a Zone
For work through phase: |  |  |  |  | As of date:
Public Agency |  |  |  | Project No.
Guideline Manager |  |  |  | Date
Project Engineer |  |  |  | Building
Project Description
NOTE: Calculation of ventilation rate per person required based on CO2 generation with an estimate of occupant activity level and maximum zone CO2 concentration of 450 ppm over outdoor. A mass balance equation for the outdoor air flow rate needed to maintain the steady-state concentration below a given limit is: Vo = N / (Cs – Co) Where: Vo = outdoor air flow rate per person N = generation rate per person Cs = CO2 concentration in the space Co = CO2 concentration in the outdoor air The formula can be further simplified, given that the guideline limit is 450 ppm over outdoor: Cs – Co = 450 ppm Reference: ASHRAE 62-2001, Appendix C and Figure C-2
TABLE 1
CO2 generation rates, per person based on activity level
ASHRAE 62-2001, Figure C-2
| N (cfm) | L/min | mets
Seated, office | 0.010943 | 0.31 | 1
Light machine | 0.01765 | 0.5 | 2
Heavy work | 0.0353 | 1 | 4
N (cfm) = L/min * 0.0353 (conversion from metric to english units)
mets = metabolic rate
TABLE 2
Ventilation Rate Required - CFM per person
| Vo | N | Cs - Co
| cfm | cfm | ppm
Seated, office | 24.3178 | 0.010943 | 0.00045
Light machine | 39.2222 | 0.01765 | 0.00045
Heavy work | 78.4444 | 0.0353 | 0.00045
450 ppm = 450 / 1,000,000 = .000450
INSTRUCTIONS
Calculator Key
BLUE - Constants or Calculated by model, Do Not Overwrite
YELLOW - User input required (Replace the sample data shown with actual)
1. Determine Co2 generation rate based on activity level of occupants in the space. Use the
graph of mets vs. CO2 generation in ASHRAE 62-2001. Figure C-2.
In the above example, the "mets" level (metabolic rate) is chosen for three activity levels and
corresponding L.min of CO2 generation is read off the Carbon Dioxide Production Line.
2. Enter the level in the L/min column of Table 1 and the corresponding cfm per person will
be calculated in the N (cfm) column.
3. Enter the N (cfm per person) in Table 2 (Ventilation Rate Required, CFM per person)
The required ventilation rate, per person (Vo) will be calculated.
NOTE:
For large areas such as gymnasiums, use an average activity level for required CFM per person.
Control of measured CO2 levels with occupancy sensors can reduce overall ventilation.